## Feuil1
Legacy
Metrology Affected by current and voltage transformers
Dec start address | Hex start address | Type | Size | Lock level | Locked fcts | Unlocked fcts
50512 | 0xC550 | Info | 62 | NONE | READ | READ
Dec address | Hex address | Words count | Description | Unit | Data type
50512 | 0xC550 | 2 | Hour Meter | h 10⁻² | U32
50514 | 0xC552 | 2 | Phase to Phase Voltage: U12 | V 10⁻² | U32
50516 | 0xC554 | 2 | Phase to Phase Voltage: U23 | V 10⁻² | U32
50518 | 0xC556 | 2 | Phase to Phase Voltage: U31 | V 10⁻² | U32
50520 | 0xC558 | 2 | Simple voltage : V1 | V 10⁻² | U32
50522 | 0xC55A | 2 | Simple voltage : V2 | V 10⁻² | U32
50524 | 0xC55C | 2 | Simple voltage : V3 | V 10⁻² | U32
50526 | 0xC55E | 2 | Frequency : F | Hz 10⁻² | U32
50528 | 0xC560 | 2 | Current : I1 | mA | U32
50530 | 0xC562 | 2 | Current : I2 | mA | U32
50532 | 0xC564 | 2 | Current : I3 | mA | U32
50534 | 0xC566 | 2 | Neutral Current : In | mA | U32
50536 | 0xC568 | 2 | Tot Active Power +/- : P | W 10 | S32
50538 | 0xC56A | 2 | Tot Reactive Power +/- : Q | var 10 | S32
50540 | 0xC56C | 2 | Tot Apparent Power : S | VA 10 | U32
50542 | 0xC56E | 2 | Tot Power Factor : -: leading et + : lagging : PF | - / 1000 | S32
50544 | 0xC570 | 2 | Active Power phase 1 +/- : P1 | W 10 | S32
50546 | 0xC572 | 2 | Active Power phase 2 +/- : P2 | W 10 | S32
50548 | 0xC574 | 2 | Active Power phase 3 +/- : P3 | W 10 | S32
50550 | 0xC576 | 2 | Reactive Power phase 1 +/- : Q1 | var 10 | S32
50552 | 0xC578 | 2 | Reactive Power phase 2 +/- : Q2 | var 10 | S32
50554 | 0xC57A | 2 | Reactive Power phase 3 +/- : Q3 | var 10 | S32
50556 | 0xC57C | 2 | Apparent Power phase 1 : S1 | VA 10 | U32
50558 | 0xC57E | 2 | Apparent Power phase 2 : S2 | VA 10 | U32
50560 | 0xC580 | 2 | Apparent Power phase 3 : S3 | VA 10 | U32
50562 | 0xC582 | 2 | Power Factor phase 1 -: leading and + : lagging : PF1 | - / 1000 | S32
50564 | 0xC584 | 2 | Power Factor phase 2 -: leading and + : lagging : PF2 | - / 1000 | S32
50566 | 0xC586 | 2 | Power Factor phase 3 -: leading and + : lagging : PF3 | - / 1000 | S32
50568 | 0xC588 | 2 | System value I Sys : (I1 + I2 + I3) / 3 | mA | U32
50570 | 0xC58A | 2 | System value U Sys : (U12 + U23 + U31 ) / 3 | V 10⁻² | U32
50572 | 0xC58C | 2 | System value V Sys : (V1 + V2 + V3 ) / 3 | V 10⁻² | U32
Energies
Dec start address | Hex start address | Type | Size | Lock level | Locked fcts | Unlocked fcts
50768 | 0xC650 | Info | 65 | NONE | READ | READ
Dec address | Hex address | Words count | Description | Unit | Data type
50768 | 0xC650 | 2 | Hour meter | h 10⁻² | U32
50770 | 0xC652 | 2 | Reserved | - | -
50772 | 0xC654 | 2 | Reserved | - | -
50774 | 0xC656 | 2 | Reserved | - | -
50776 | 0xC658 | 2 | Reserved | - | -
50778 | 0xC65A | 2 | Reserved | - | -
50780 | 0xC65C | 2 | Partial Positive Active Energy: Ea+ | kWh | U32
50782 | 0xC65E | 2 | Partial Positive Reactive Energy: Er + | varh 10³ | U32
50784 | 0xC660 | 2 | Partial Apparent Energy : Es | kVAh | U32
50786 | 0xC662 | 2 | Partial Negative Active Energy : Ea- | kWh | U32
50788 | 0xC664 | 2 | Partial Negative Reactive Energy : Er - | varh 10³ | U32
50790 | 0xC666 | 2 | Number of pulse meter (3 Maxi) | - | U32
50792 | 0xC668 | 2 | Total pulse meter Input 1 | - | U32
50794 | 0xC66A | 2 | Total pulse meter Input 2 | - | U32
50796 | 0xC66C | 2 | Total pulse meter Input 3 | - | U32
50798 | 0xC66E | 2 | Reserved | - | -
50800 | 0xC670 | 2 | Reserved | - | -
50802 | 0xC672 | 2 | Reserved | - | -
50804 | 0xC674 | 2 | Reserved | - | -
50806 | 0xC676 | 2 | Reserved | - | -
50808 | 0xC678 | 2 | Reserved | - | -
50810 | 0xC67A | 2 | Reserved | - | -
50812 | 0xC67C | 2 | Predictive Active Power | W 10 | U32
50814 | 0xC67E | 2 | Predictive Reactive Power | var 10 | U32
50816 | 0xC680 | 2 | Predictive Apparent Power | VA 10 | U32
50818 | 0xC682 | 2 | Reserved | - | -
50820 | 0xC684 | 2 | Reserved | - | -
50822 | 0xC686 | 2 | Reserved | - | -
50824 | 0xC688 | 2 | Reserved | - | -
50826 | 0xC68A | 2 | Reserved | - | -
50828 | 0xC68C | 1 | Reserved | - | -
50829 | 0xC68D | 1 | Reserved | - | -
50830 | 0xC68E | 1 | Reserved | - | -
50831 | 0xC68F | 1 | Reserved | - | -
50832 | 0xC690 | 1 | Reserved | - | -
RAZ ( Function 6 )
Dec start address | Hex start address | Type | Size | Lock level | Locked fcts | Unlocked fcts
1024 | 0x0400 | Commands | 4 | NONE | WRITE | WRITE
Dec address | Hex address | Words count | Description | Unit | Data type
1024 | 0x0400 | 1 | Reset 1 (0xFFFF for all) | - | U16_HEX
0x1000 : All energies
1025 | 0x0401 | 1 | Reserved | - | -
1026 | 0x0402 | 1 | Reserved | - | -
1027 | 0x0403 | 1 | Reserved | - | -